# Day 2 — Transformer Loading and Energy Analysis

## System

Grid voltage = 11 kV

Transformer = 11/0.415 kV

Transformer rating = 1000 kVA

LV voltage = 415 V

Frequency = 50 Hz

## Total Load

Total active power = 650 kW

Total reactive power ≈ 380.12 kVAR

Total apparent power ≈ 752.99 kVA

Overall power factor ≈ 0.863

## Transformer Loading

Transformer loading:

Loading (%) = S_load / S_rated × 100

Approximate loading = 75.3%

## Transformer Currents

Three-phase current:

I = S/(sqrt(3)V)

LV full-load current ≈ 1391 A

HV full-load current ≈ 52.5 A

Actual LV current ≈ 1048 A

## Transformer Losses

Core loss = 2.5 kW

Rated copper loss = 10 kW

Copper loss at partial load:

Pcu = x² Pcu,rated

where:

x = S_load/S_rated

## Efficiency

η = Pout/(Pout + Ploss) × 100

Approximate efficiency ≈ 98.8%

## Energy Analysis

Average power:

Pavg = Rated Power × Load Factor

Daily energy:

Eday = Pavg × Operating Hours

Monthly energy:

Emonth = Eday × 30

## Day 2 Completed

- Updated industrial load dataset

- Added load factor

- Added operating hours

- Built energy analysis module

- Built transformer analysis module

- Calculated transformer loading

- Calculated HV/LV current

- Calculated transformer losses

- Calculated transformer efficiency

- Added transformer status

- Created transformer loading graphs

- Validated calculations using MATLAB