# Day 3 — Power Factor Correction

## Initial System

Active Power = 650 kW

Reactive Power ≈ 380.12 kVAR

Apparent Power ≈ 752.99 kVA

Original PF ≈ 0.863

Transformer Rating = 1000 kVA

Original Transformer Loading ≈ 75.3%

## Power Factor Correction

Target PF = 0.95

Required capacitor compensation ≈ 126 kVAR

Selected practical capacitor bank = 125 kVAR

## After Compensation

New Reactive Power ≈ 255.12 kVAR

New Apparent Power ≈ 698 kVA

New PF ≈ 0.931

LV Current decreases from approximately 1048 A to approximately 972 A.

Transformer loading decreases from approximately 75.3% to approximately 69.8%.

## Important Equations

PF = P/S

S = sqrt(P² + Q²)

Qc = P(tan(phi1) - tan(phi2))

Qnew = Qload - Qc

Snew = sqrt(P² + Qnew²)

I = S/(sqrt(3)V)

## Engineering Concept

Power factor correction reduces reactive power, apparent power and supply current while active power remains approximately unchanged.

## Day 3 Completed

- Power factor analysis

- Power triangle

- Capacitor kVAR calculation

- Practical capacitor-bank selection

- Post-correction reactive power

- Post-correction apparent power

- Post-correction power factor

- Current reduction

- Transformer loading reduction

- PF sensitivity analysis

- Python implementation

- MATLAB implementation

- Engineering graphs